## Slide 1: Winter Storm URI
Presented by:
MACKENZIE OSBORNE
JEREMY WEBER
MITCH PAGE
WILL GUTOWSKY
BRIDGELAND
Notes: Introduce topic
Introduce speakers
Remind them about how the Chat
Remind them about delay (about 20 seconds)
Opportunities to answers questions in between slides

## Slide 2: Winter Storm URI
Inframark Winter Prep
URI Timeline Review
URI Facts/Summary
Triage
Boil Water Notice
& Communication
Lessons Learned
Notes: Todd

## Slide 3: Inframark Operations Winter Prep
Winterization program begins in September of each year
We have a process for both water and wastewater plants:
  Initial audit performed by operator
  Operator identifies new items that need to be winterized
  Operator identifies winterization that needs replacement
  Materials are obtained and those items are winterized
  Manager then visits the facility and inspects before signing off
Notes: Steelman

## Slide 4: Inframark Pre-URI Action item
Top off fuel tanks
Isolated nonessential water lines (eye wash stations, etc.)
Contact suppliers
Opened drain and drip lines
Checked lights in HPT
Doubled checked insulation on all exposed areas.
Notes: Opened drain pipes, hose bibs, topped off fueled

## Slide 5: URI Timeline-General Facts
Notes: Todd

## Slide 6: February 14, 2021
Notes: Todd

## Slide 7: URI Facts-General
Notes: Todd

## Slide 8: URI Facts-IAH
Notes: todd

## Slide 9: URI SUMMARY- General
The Winter Outbreak that occurred on Valentine's Week 2021 brought not only snow, sleet, and freezing rain to Southeast Texas, but also extreme cold temperatures that lasted for several days. This was one of the most impactful winter events in recent history that brought multiday road closures, power outages, loss of heat, broken pipes, and other societal impacts for the region. While the damage is still being assessed, this will likely go down as the first billion-dollar disaster of 2021 globally, and potentially the costliest weather disaster for the state of Texas in history, surpassing even Hurricane Harvey from 2017.
Notes: Todd

## Slide 10
Notes: Joe/Kristi

## Slide 11
Notes: Padalino

## Slide 12: Triage- Bridgeland
Hotel room during event for all staff to take rest periods
Multiple employees in rotation in field
Every three hours a Bridgeland facility walk through was performed:
  Operator checked hose bibs, valve casings, HPTs,etc.
Notes: Steelman

## Slide 13: ARS Triage
Fuel Deliveries
Inframark had (2) 5,000-gallon bobtail fuel tanker trucks
60 ARS scheduled fuel deliveries were made to Inframark facilities. No ARS supported facilities went down due to lack of fuel
Over 28,000 gallons of diesel delivered
Bridgeland generators did not run out of fuel
ARS Freeze Work Order Analysis-421 Work Orders
Chart: 
| Water Plant | Sewer Plant | Lift Station | Storm Water | Sewer Maint | Water Maint
WO Count | 232 | 102 | 76 | 3 | 4 | 4
Notes: Padalino

## Slide 14: ARS Triage
Types of Work Performed
Frozen sensor lines
Frozen analog level/PSI transducers
Frozen intake lines on non-potable water systems
Frozen discharge lines on submersible water wells
Frozen cracked pump housing
Frozen valves
Control power issues
Generator issues –
  Waterplant #1-
    LOST COOLANT LONE FROM GENSET RADIATOR.
    ATS-FLUCUATION IN AC POWER CAUSED THE SWITCH TO NOT OPERATE IN AUTO PROPOERLY
Notes: Padalino/ Steelman

## Slide 15: Batteries and cold weather
Notes: Padalino

## Slide 16: Boil Water Notice
Definition
Notification
  Beginning
  Rescind
Consecutive System
Notes: Yentzen to present this slide

## Slide 17
Notes: Yentzen

## Slide 18
Notes: Yentzen

## Slide 19: Water Plant Breakdown
Water Plant #1 services HC419
Water Plant #2 services HC489 and portions of HC419
  419 Sections include:
Bedias Creek
  Madison Midway
  Bullard Creek
  Cancy Creek
  Busy Bee
Cibolo Creek
  Tapalcomes Dr
  Highland Country
  Fort Leaton
  Copper Lantern
Barton Creek
  Blueberry Cedar
  Blackcap Viero
  Hays Spring
  Ladybird Lake
  Brickelbush Lake
  Maravillas Cove
Cedar Creek
  Maifest
  Texas Lancer
  Covey Trail
  Trinity River
  Astin Mansion

## Slide 20: Timeline: Water Plant #1
11:48 PM
First loss of control power
9:16 AM WHCRWA no longer supplying surface water
2:55 PM First alert of low GST level
5:42 PM
HC419 BWN
7:30 PM HC419 Water Outage
5:46 PM Water restored
5:49 PM Generator coolant line broke
10:15 PM Second Water Outage
8:30 AM Water restored
Surface water returned 2/22/2021
HC419 BWN rescinded 2/22/2021
2:15 PM First alert of low EST
60
40
20
Notes: 7:30 Water Outage- GST at 5ft, turned wells off to refill tanks over night. Power issues throughout the night
Jeremy, why didn’t the generator run the night of 2/16 when we needed to refill the tanks? ATS and coolant problems. See below.
Why were we able to meet demand without surface water from 2/18 to 2/22? Less usage, I believe the community knew we were in serious trouble and they acted more conservatively a lot of leaks were isolated after the first hard freeze/thaw.
When did we have issues with the transfer switch? 2/16 and 2/17 2 times each day we had ATS transfer issues as well as Gen coolant issues. Power unreliable and couldn’t travel to get the water restored. Main normal power came back on 2/17 in afternoon. We were able to fill GSTs, gen down due to coolant problems until 2/18. Normal power on during that time but demand was too high for well capacity. Shut down in the evening of the 17th and restored water 2/18(demand was low therafter)

## Slide 21: Timeline: Water Plant #2
10:31 PM Low level
11:20 PM Water Outage
7:15 PM
Water restored
4:50 PM
Water plant manually operated
60
40
20
BWN
Notes: When did we issue the 489 BWN? 2/17 the BWN was issued according to VC email. Power was off for an extended period of time and the Gen does not operate the WP2 onsite well.

## Slide 22: Lessons Learned
Enhanced/Extreme Winterization of plant equipment
Install heat trace tape, insulate and wrap all piping & valves
Install heat lamps in areas that could possibly freeze
Insulate HPT dog houses
Install heat jacket on pumps and flow control valves
Install heaters in water supply/ chlorine feed rooms with thermometer (FZ can monitor)
Drain and isolate eyewash stations
Notes: Padalino

## Slide 23: Lessons
  Water Well #3 not on generator power
  Water plant #2 generator only runs 2 booster pumps
        New generator is on site waiting to be tied in
        Water well #3 has sound attenuator. Best case scenario would be a day to get it off.
Notes: Padalino

## Slide 24: Steps moving forward
Encourage a more unified BWN system that is controlled via the state or the county.
Encourage a CoH communication protocol that would alert RWA of potential outages to prevent BWN from RWA participants.
Encourage a community wide education platform to inform end users about BWN.
Encourage Districts to consider signage.
Push notifications.
Communication Protocol.
Evaluate extreme winterization options.
Notes: Burrer

## Slide 25: Questions?? Thank you
Inframark, LC
Texas MUD Leadership Team
Notes: Burrer